## General
Study ID | muranga x feeder
Study Case ID | LF
Data Revision | Base
Configuration | Normal
Loading Cat | Design
Generation Cat | Design
Diversity Factor | Normal Loading
Buses | 232
Branches | 231
Generators | 0
Power Grids | 1
Loads | 92
Load-MW | 6.096
Load-Mvar | 3.778
Generation-MW | 6.11
Generation-Mvar | 4.198
Loss-MW | 0.014
Loss-Mvar | 0.42
Mismatch-MW | 0
Mismatch-Mvar | 0

## Bus
Bus ID | Nominal kV | Voltage | MW Loading | Mvar Loading
Bus788 | 0.415 | 95.45 | 0.029 | 0.018
Bus789 | 11 | 96.27 | 0.0291 | 0.0185
Bus790 | 0.415 | 96.25 | 0.003 | 0.0019
Bus791 | 11 | 96.27 | 0.003 | 0.0019
Bus792 | 0.415 | 95.23 | 0.182 | 0.113
Bus793 | 11 | 96.27 | 0.182 | 0.117
Bus794 | 0.415 | 96.22 | 0.0093 | 0.0058
Bus795 | 11 | 96.27 | 0.191 | 0.123
Bus796 | 0.415 | 96.22 | 0.0089 | 0.0055
Bus797 | 11 | 96.27 | 0.2 | 0.128
Bus798 | 11 | 96.27 | 0.203 | 0.13
Bus799 | 0.415 | 96.22 | 0.0093 | 0.0058
Bus800 | 11 | 96.27 | 0.0093 | 0.0058
Bus801 | 11 | 96.27 | 0.213 | 0.136
Bus802 | 0.415 | 96.19 | 0.003 | 0.0019
Bus803 | 11 | 96.27 | 0.216 | 0.138
Bus804 | 11 | 96.27 | 0.245 | 0.156
Bus805 | 0.415 | 96.19 | 0.003 | 0.0019
Bus806 | 11 | 96.27 | 0.003 | 0.0019
Bus807 | 11 | 96.27 | 0.248 | 0.158
Bus808 | 0.415 | 98.01 | 0.193 | 0.119
Bus809 | 11 | 98.1 | 0.193 | 0.12
Bus810 | 0.415 | 98.02 | 0.193 | 0.119
Bus811 | 11 | 98.1 | 0.193 | 0.12
Bus812 | 11 | 98.1 | 0.385 | 0.24
Bus813 | 0.415 | 98.02 | 0.0612 | 0.038
Bus814 | 11 | 98.1 | 0.447 | 0.278
Bus815 | 0.415 | 97.98 | 0.193 | 0.119
Bus816 | 11 | 98.07 | 0.193 | 0.12
Bus817 | 0.415 | 97.97 | 0.122 | 0.0758
Bus818 | 0.415 | 97.96 | 0.122 | 0.0758
Bus819 | 11 | 98.05 | 0.122 | 0.076
Bus820 | 0.415 | 97.96 | 0.122 | 0.0758
Bus821 | 11 | 98.05 | 0.122 | 0.076
Bus822 | 11 | 98.05 | 0.245 | 0.152
Bus823 | 11 | 98.05 | 0.367 | 0.228
Bus824 | 0.415 | 97.97 | 0.193 | 0.119
Bus825 | 11 | 98.05 | 0.193 | 0.12
Bus826 | 0.415 | 97.94 | 0.0612 | 0.0379
Bus827 | 0.415 | 97.94 | 0.193 | 0.12
Bus828 | 11 | 98.02 | 0.193 | 0.12
Bus829 | 11 | 98.02 | 1.473 | 0.919
Bus830 | 11 | 98.02 | 1.534 | 0.957
Bus831 | 0.415 | 97.93 | 0.193 | 0.12
Bus832 | 0.415 | 93.7 | 0.177 | 0.11
Bus833 | 11 | 93.79 | 0.177 | 0.11
Bus834 | 0.415 | 93.7 | 0.177 | 0.11
Bus835 | 0.415 | 91.29 | 0.195 | 0.121
Bus836 | 11 | 91.38 | 0.195 | 0.121
Bus837 | 0.415 | 93.7 | 0.177 | 0.11
Bus838 | 11 | 93.78 | 0.177 | 0.11
Bus839 | 11 | 93.78 | 0.372 | 0.242
Bus840 | 11 | 93.78 | 0.549 | 0.352
Bus841 | 0.415 | 100.11 | 0.202 | 0.125
Bus842 | 11 | 93.78 | 0.202 | 0.127
Bus843 | 11 | 93.78 | 0.751 | 0.479
Bus844 | 0.415 | 93.7 | 0.0622 | 0.0385
Bus845 | 11 | 93.78 | 0.813 | 0.518
Bus846 | 0.415 | 93.7 | 0.177 | 0.11
Bus847 | 0.415 | 93.7 | 0.177 | 0.11
Bus848 | 11 | 93.78 | 0.177 | 0.11
Bus849 | 11 | 93.78 | 1.167 | 0.738
Bus850 | 11 | 93.79 | 1.343 | 0.848
Bus851 | 0.415 | 97.93 | 0.122 | 0.0758
Bus852 | 0.415 | 97.9 | 0.0092 | 0.0057
Bus853 | 0.415 | 97.9 | 0.0611 | 0.0379
Bus854 | 0.415 | 97.93 | 0.0096 | 0.006
Bus855 | 0.415 | 97.23 | 0.0804 | 0.0498
Bus856 | 0.415 | 97.89 | 0.0081 | 0.005
Bus857 | 11 | 97.97 | 0.0081 | 0.0051
Bus858 | 0.415 | 97.89 | 0.0305 | 0.0189
Bus859 | 11 | 97.97 | 0.0387 | 0.024
Bus860 | 0.415 | 97.89 | 0.0092 | 0.0057
Bus861 | 11 | 97.97 | 0.0092 | 0.0057
Bus862 | 0.415 | 97.9 | 0.0815 | 0.0505
Bus863 | 11 | 97.97 | 0.0907 | 0.0563
Bus864 | 11 | 97.97 | 0.129 | 0.0804
Bus865 | 11 | 97.98 | 0.21 | 0.131
Bus866 | 11 | 97.98 | 0.219 | 0.137
Bus867 | 0.415 | 97.89 | 0.0306 | 0.0189
Bus868 | 0.415 | 97.89 | 0.0316 | 0.0196
Bus869 | 11 | 97.97 | 0.0316 | 0.0196
Bus870 | 0.415 | 97.23 | 0.0804 | 0.0498
Bus871 | 11 | 97.97 | 0.0804 | 0.0511
Bus872 | 0.415 | 97.89 | 0.0305 | 0.0189
Bus873 | 11 | 97.98 | 0.0305 | 0.019
Bus874 | 11 | 97.98 | 0.111 | 0.07
Bus875 | 11 | 97.98 | 0.143 | 0.0897
Bus876 | 11 | 97.98 | 0.173 | 0.109
Bus877 | 0.415 | 97.9 | 0.0153 | 0.0095
Bus878 | 11 | 97.98 | 0.0153 | 0.0095
Bus879 | 11 | 97.98 | 0.188 | 0.118
Bus880 | 0.415 | 97.9 | 0.0153 | 0.0095
Bus881 | 11 | 97.98 | 0.0153 | 0.0095
Bus882 | 11 | 97.98 | 0.204 | 0.128
Bus883 | 11 | 97.98 | 0.423 | 0.265
Bus884 | 0.415 | 97.93 | 0.0096 | 0.006
Bus885 | 11 | 97.98 | 0.0096 | 0.006
Bus886 | 0.415 | 97.9 | 0.0092 | 0.0057
Bus887 | 11 | 97.98 | 0.0092 | 0.0057
Bus888 | 11 | 97.98 | 0.0188 | 0.0117
Bus889 | 11 | 97.98 | 0.503 | 0.315
Bus890 | 0.415 | 97.21 | 0.0841 | 0.0521
Bus891 | 11 | 97.99 | 0.0841 | 0.0535
Bus892 | 11 | 97.99 | 0.587 | 0.368
Bus893 | 11 | 97.99 | 0.596 | 0.374
Bus894 | 0.415 | 97.91 | 0.0611 | 0.0379
Bus895 | 11 | 97.99 | 0.0611 | 0.038
Bus896 | 11 | 97.99 | 0.658 | 0.412
Bus897 | 0.415 | 97.91 | 0.0611 | 0.0379
Bus898 | 11 | 98 | 0.0611 | 0.038
Bus899 | 11 | 98 | 0.719 | 0.45
Bus900 | 11 | 98.01 | 0.841 | 0.526
Bus901 | 0.415 | 97.93 | 0.192 | 0.119
Bus902 | 415 | 97.93 | 0.192 | 0.119
Bus903 | 11 | 98.01 | 0.192 | 0.12
Bus904 | 11 | 98.01 | 0.385 | 0.239
Bus905 | 11 | 98.01 | 1.226 | 0.766
Bus906 | 11 | 98.02 | 2.764 | 1.86
Bus907 | 11 | 98.03 | 4.298 | 2.817
Bus908 | 0.415 | 97.95 | 0.0031 | 0.0019
Bus909 | 11 | 98.03 | 4.301 | 2.82
Bus910 | 0.415 | 97.67 | 0.0842 | 0.0522
Bus911 | 11 | 98.04 | 0.0842 | 0.0528
Bus912 | 11 | 98.04 | 4.385 | 2.873
Bus913 | 11 | 98.05 | 4.945 | 3.222
Bus914 | 11 | 98.07 | 5.137 | 3.344
Bus915 | 11 | 98.1 | 5.584 | 3.625
Bus916 | 0.415 | 97.87 | 0.0843 | 0.0522
Bus917 | 11 | 98.1 | 5.668 | 3.678
Bus918 | 0.415 | 97.61 | 0.0607 | 0.0376
Bus919 | 11 | 98.16 | 0.0608 | 0.0384
Bus920 | 11 | 98.16 | 5.729 | 3.724
Bus921 | 11 | 98.18 | 5.977 | 3.894
Bus922 | 11 | 98.19 | 6.068 | 3.954
Bus923 | 11 | 98.23 | 6.068 | 3.959
Bus924 | 0.415 | 97.95 | 0.0306 | 0.019
Bus925 | 11 | 98.23 | 6.099 | 3.978
Bus926 | 33 | 100 | 6.11 | 4.198
Bus931 | 0.415 | 97.35 | 0.091 | 0.0564
Bus932 | 11 | 98.02 | 1.279 | 0.799
Bus934 | 0.415 | 97.94 | 0.0306 | 0.0189
Bus935 | 11 | 98.02 | 1.249 | 0.78
Bus936 | 0.415 | 97.93 | 0.0459 | 0.0284
Bus937 | 11 | 98.01 | 1.203 | 0.751
Bus940 | 0.415 | 97.42 | 0.0605 | 0.0375
Bus941 | 11 | 98 | 1.142 | 0.713
Bus946 | 11 | 98 | 0.0304 | 0.019
Bus947 | 0.415 | 97.71 | 0.0304 | 0.0189
Bus948 | 0.415 | 97.92 | 0.0306 | 0.0189
Bus949 | 11 | 98 | 1.081 | 0.674
Bus950 | 0.415 | 97.92 | 0.0092 | 0.0057
Bus951 | 11 | 97.98 | 1.072 | 0.668
Bus952 | 0.415 | 97.24 | 0.0804 | 0.0498
Bus953 | 11 | 97.97 | 0.992 | 0.617
Bus955 | 0.415 | 97.89 | 0.0092 | 0.0057
Bus957 | 0.415 | 97.89 | 0.122 | 0.0757
Bus958 | 11 | 97.96 | 0.86 | 0.535
Bus959 | 11 | 97.96 | 0.154 | 0.0962
Bus960 | 0.415 | 97.88 | 0.0092 | 0.0057
Bus961 | 11 | 97.96 | 0.145 | 0.0905
Bus962 | 0.415 | 97.93 | 0.0096 | 0.006
Bus964 | 11 | 97.96 | 0.136 | 0.0845
Bus965 | 0.415 | 97.7 | 0.0957 | 0.0593
Bus966 | 11 | 97.96 | 0.0398 | 0.0247
Bus974 | 11 | 97.96 | 0.0092 | 0.0057
Bus976 | 0.415 | 97.87 | 0.0092 | 0.0057
Bus977 | 11 | 97.96 | 0.0306 | 0.019
Bus978 | 0.415 | 97.94 | 0.0306 | 0.019
Bus979 | 11 | 97.97 | 0.0092 | 0.0057
Bus980 | 11 | 97.95 | 0.706 | 0.439
Bus981 | 0.415 | 97.79 | 0.0572 | 0.0355
Bus982 | 11 | 97.95 | 0.649 | 0.403
Bus983 | 11 | 97.95 | 0.0857 | 0.0532
Bus985 | 11 | 97.95 | 0.0153 | 0.0095
Bus986 | 0.415 | 97.87 | 0.0153 | 0.0095
Bus987 | 11 | 97.95 | 0.0704 | 0.0437
Bus991 | 11 | 97.95 | 0.0153 | 0.0095
Bus992 | 0.415 | 97.87 | 0.0153 | 0.0095
Bus993 | 11 | 97.95 | 0.0551 | 0.0342
Bus994 | 11 | 97.95 | 0.0398 | 0.0247
Bus996 | 11 | 97.95 | 0.0306 | 0.019
Bus999 | 0.415 | 97.87 | 0.0092 | 0.0057
Bus1000 | 0.415 | 97.91 | 0.0306 | 0.0189
Bus1002 | 11 | 97.95 | 0.0153 | 0.0095
Bus1003 | 0.415 | 97.87 | 0.0153 | 0.0095
Bus1004 | 11 | 97.95 | 0.563 | 0.35
Bus1005 | 11 | 97.95 | 0.0642 | 0.0399
Bus1008 | 11 | 97.95 | 0.0031 | 0.0019
Bus1009 | 0.415 | 97.86 | 0.0031 | 0.0019
Bus1010 | 11 | 97.95 | 0.0611 | 0.0379
Bus1011 | 11 | 97.95 | 0.0305 | 0.019
Bus1012 | 0.415 | 97.86 | 0.0305 | 0.0189
Bus1013 | 11 | 97.95 | 0.0305 | 0.019
Bus1015 | 0.415 | 97.86 | 0.0305 | 0.0189
Bus1016 | 11 | 97.95 | 0.499 | 0.31
Bus1018 | 11 | 97.95 | 0.0305 | 0.019
Bus1019 | 0.415 | 97.86 | 0.0305 | 0.0189
Bus1020 | 11 | 97.94 | 0.468 | 0.291
Bus1022 | 11 | 97.94 | 0.122 | 0.0759
Bus1023 | 0.415 | 97.86 | 0.122 | 0.0757
Bus1024 | 11 | 97.94 | 0.346 | 0.215
Bus1025 | 11 | 97.94 | 0.0713 | 0.0442
Bus1026 | 11 | 97.94 | 0.0407 | 0.0253
Bus1027 | 11 | 97.94 | 0.0306 | 0.019
Bus1028 | 0.415 | 97.91 | 0.0407 | 0.0253
Bus1030 | 0.415 | 97.91 | 0.0306 | 0.0189
Bus1031 | 11 | 97.94 | 0.275 | 0.171
Bus1034 | 0.415 | 97.92 | 0.0611 | 0.0379
Bus1035 | 11 | 97.94 | 0.214 | 0.133
Bus1036 | 0.415 | 97.85 | 0.0153 | 0.0095
Bus1041 | 11 | 97.94 | 0.0153 | 0.0095
Bus1042 | 0.415 | 97.85 | 0.0153 | 0.0095
Bus1043 | 11 | 97.94 | 0.183 | 0.114
Bus1045 | 11 | 97.94 | 0.0305 | 0.019
Bus1046 | 0.415 | 97.85 | 0.0305 | 0.0189
Bus1047 | 11 | 97.93 | 0.153 | 0.0949
Bus1049 | 11 | 97.93 | 0.0305 | 0.019
Bus1050 | 0.415 | 97.85 | 0.0305 | 0.0189
Bus1051 | 11 | 97.93 | 0.122 | 0.0759
Bus1052 | 11 | 97.93 | 0.0305 | 0.019
Bus1053 | 0.415 | 97.85 | 0.0305 | 0.0189
Bus1054 | 11 | 97.93 | 0.0917 | 0.0569
Bus1055 | 11 | 97.93 | 0.0305 | 0.019
Bus1056 | 0.415 | 97.85 | 0.0305 | 0.0189
Bus1057 | 11 | 97.93 | 0.0612 | 0.038
Bus1058 | 11 | 97.93 | 0.0153 | 0.0095
Bus1060 | 0.415 | 97.85 | 0.0153 | 0.0095
Bus1061 | 11 | 97.93 | 0.0459 | 0.0285
Bus1063 | 0.415 | 97.89 | 0.0305 | 0.0189
Bus1064 | 11 | 97.93 | 0.0153 | 0.0095
Bus1065 | 0.415 | 97.89 | 0.0153 | 0.0095

## Branch
ID | Bus 1 | Bus 2 | Type | Allowable | MW Flow | Mvar Flow | Amp Flow | % PF | % Loading | % Voltage Drop | kW Losses | kvar Losses
Cable436 | Bus789 | Bus804 | Cable | 0 A | 0.0291 | 0.0185 | 1.879 | 84.35 |  | 0 | 0 | 0.0001
Cable437 | Bus798 | Bus791 | Cable | 0 A | 0.003 | 0.0019 | 0.192 | 84.99 |  | 0 | 0 | 0
Cable438 | Bus795 | Bus793 | Cable | 0 A | 0.182 | 0.117 | 11.8 | 84.18 |  | 0 | 0 | 0.002
Cable439 | Bus797 | Bus795 | Cable | 0 A | 0.191 | 0.123 | 12.39 | 84.22 |  | 0 | 0 | 0.004
Cable440 | Bus798 | Bus797 | Cable | 0 A | 0.2 | 0.128 | 12.96 | 84.25 |  | 0 | 0.0001 | 0.0113
Cable441 | Bus801 | Bus798 | Cable | 0 A | 0.203 | 0.13 | 13.15 | 84.26 |  | 0 | 0 | 0.0035
Cable442 | Bus801 | Bus800 | Cable | 0 A | 0.0093 | 0.0058 | 0.596 | 84.96 |  | 0 | 0 | 0
Cable443 | Bus803 | Bus801 | Cable | 0 A | 0.213 | 0.136 | 13.75 | 84.29 |  | 0 | 0.0001 | 0.0052
Cable444 | Bus804 | Bus803 | Cable | 0 A | 0.216 | 0.138 | 13.94 | 84.3 |  | 0 | 0 | 0.0007
Cable445 | Bus807 | Bus804 | Cable | 0 A | 0.245 | 0.156 | 15.82 | 84.3 |  | 0 | 0.0001 | 0.0074
Cable446 | Bus806 | Bus807 | Cable | 0 A | 0.003 | 0.0019 | 0.192 | 84.93 |  | 0 | 0 | 0
Cable447 | Bus921 | Bus807 | Cable | 0 A | 0.248 | 0.168 | 16.01 | 82.71 |  | 1.9 | 0.104 | 10.4
Cable448 | Bus812 | Bus809 | Cable | 0 A | 0.193 | 0.12 | 12.14 | 84.93 |  | 0 | 0 | 0.0021
Cable449 | Bus812 | Bus811 | Cable | 0 A | 0.193 | 0.12 | 12.14 | 84.94 |  | 0 | 0 | 0.0002
Cable450 | Bus812 | Bus814 | Cable | 0 A | 0.385 | 0.24 | 24.28 | 84.93 |  | 0 | 0.0001 | 0.0134
Cable451 | Bus814 | Bus915 | Cable | 0 A | 0.447 | 0.278 | 28.14 | 84.93 |  | 0 | 0.0002 | 0.0188
Cable452 | Bus816 | Bus914 | Cable | 0 A | 0.193 | 0.12 | 12.14 | 84.93 |  | 0 | 0 | 0.0017
Cable453 | Bus822 | Bus819 | Cable | 0 A | 0.122 | 0.076 | 7.713 | 84.93 |  | 0 | 0 | 0.001
Cable454 | Bus822 | Bus821 | Cable | 0 A | 0.122 | 0.076 | 7.713 | 84.93 |  | 0 | 0 | 0.0007
Cable455 | Bus823 | Bus822 | Cable | 0 A | 0.245 | 0.152 | 15.43 | 84.93 |  | 0 | 0.0001 | 0.0079
Cable456 | Bus823 | Bus913 | Cable | 0 A | 0.367 | 0.228 | 23.14 | 84.93 |  | 0 | 0.0001 | 0.0106
Cable457 | Bus825 | Bus913 | Cable | 0 A | 0.193 | 0.12 | 12.13 | 84.93 |  | 0 | 0 | 0.0012
Cable458 | Bus829 | Bus828 | Cable | 0 A | 0.193 | 0.12 | 12.18 | 84.93 |  | 0 | 0 | 0.0011
Cable459 | Bus829 | Bus830 | Cable | 0 A | 1.473 | 0.919 | 92.95 | 84.84 |  | 0 | 0.0007 | 0.0715
Cable460 | Bus830 | Bus907 | Cable | 0 A | 1.534 | 0.957 | 96.8 | 84.84 |  | 0 | 0.0008 | 0.0776
Cable461 | Bus850 | Bus833 | Cable | 0 A | 0.177 | 0.11 | 11.66 | 84.93 |  | 0 | 0 | 0.0002
Cable462 | Bus839 | Bus836 | Cable | 0 A | 0.195 | 0.132 | 13.17 | 82.8 |  | 2.39 | 0.109 | 10.86
Cable463 | Bus839 | Bus838 | Cable | 0 A | 0.177 | 0.11 | 11.66 | 84.93 |  | 0 | 0 | 0.0015
Cable464 | Bus840 | Bus839 | Cable | 0 A | 0.372 | 0.242 | 24.82 | 83.82 |  | 0 | 0.0001 | 0.01
Cable465 | Bus843 | Bus840 | Cable | 0 A | 0.549 | 0.352 | 36.48 | 84.18 |  | 0 | 0.0002 | 0.0216
Cable466 | Bus842 | Bus843 | Cable | 0 A | 0.202 | 0.127 | 13.37 | 84.58 |  | 0 | 0 | 0.0005
Cable467 | Bus845 | Bus843 | Cable | 0 A | 0.751 | 0.479 | 49.84 | 84.28 |  | 0 | 0.0008 | 0.0836
Cable468 | Bus845 | Bus849 | Cable | 0 A | 0.813 | 0.518 | 53.94 | 84.33 |  | 0 | 0.0002 | 0.0166
Cable469 | Bus849 | Bus848 | Cable | 0 A | 0.177 | 0.11 | 11.66 | 84.93 |  | 0 | 0 | 0.0026
Cable470 | Bus850 | Bus849 | Cable | 0 A | 1.167 | 0.738 | 77.25 | 84.51 |  | 0 | 0.0001 | 0.0082
Cable471 | Bus906 | Bus850 | Cable | 0 A | 1.345 | 0.974 | 88.91 | 80.99 |  | 4.23 | 1.26 | 126
Cable472 | Bus857 | Bus859 | Cable | 0 A | 0.0081 | 0.0051 | 0.514 | 84.93 |  | 0.01 | 0 | 0.0016
Cable473 | Bus859 | Bus864 | Cable | 0 A | 0.0387 | 0.024 | 2.441 | 84.93 |  | 0 | 0 | 0.0001
Cable474 | Bus861 | Bus863 | Cable | 0 A | 0.0092 | 0.0057 | 0.581 | 84.93 |  | 0 | 0 | 0
Cable475 | Bus864 | Bus863 | Cable | 0 A | 0.0907 | 0.0563 | 5.719 | 84.94 |  | 0 | 0 | 0.0004
Cable476 | Bus865 | Bus864 | Cable | 0 A | 0.129 | 0.0804 | 8.16 | 84.94 |  | 0 | 0 | 0.0047
Cable477 | Bus866 | Bus865 | Cable | 0 A | 0.21 | 0.131 | 13.26 | 84.74 |  | 0 | 0.0002 | 0.0189
Cable478 | Bus883 | Bus866 | Cable | 0 A | 0.219 | 0.137 | 13.87 | 84.75 |  | 0 | 0.0001 | 0.0071
Cable479 | Bus875 | Bus869 | Cable | 0 A | 0.0316 | 0.0196 | 1.994 | 84.93 |  | 0 | 0 | 0.0007
Cable480 | Bus874 | Bus871 | Cable | 0 A | 0.0804 | 0.0511 | 5.103 | 84.42 |  | 0 | 0 | 0.0043
Cable481 | Bus874 | Bus873 | Cable | 0 A | 0.0305 | 0.019 | 1.927 | 84.93 |  | 0 | 0 | 0
Cable482 | Bus875 | Bus874 | Cable | 0 A | 0.111 | 0.07 | 7.03 | 84.56 |  | 0 | 0 | 0.0019
Cable483 | Bus876 | Bus875 | Cable | 0 A | 0.143 | 0.0897 | 9.024 | 84.64 |  | 0 | 0.0001 | 0.0069
Cable484 | Bus879 | Bus876 | Cable | 0 A | 0.173 | 0.109 | 10.95 | 84.69 |  | 0 | 0.0001 | 0.0098
Cable485 | Bus879 | Bus878 | Cable | 0 A | 0.0153 | 0.0095 | 0.966 | 84.93 |  | 0 | 0 | 0
Cable486 | Bus882 | Bus879 | Cable | 0 A | 0.188 | 0.118 | 11.92 | 84.71 |  | 0 | 0 | 0.001
Cable487 | Bus882 | Bus881 | Cable | 0 A | 0.0153 | 0.0095 | 0.966 | 84.93 |  | 0 | 0 | 0
Cable488 | Bus883 | Bus882 | Cable | 0 A | 0.204 | 0.128 | 12.88 | 84.73 |  | 0 | 0 | 0.0032
Cable489 | Bus889 | Bus883 | Cable | 0 A | 0.423 | 0.265 | 26.75 | 84.73 |  | 0 | 0.0002 | 0.0168
Cable490 | Bus885 | Bus888 | Cable | 0 A | 0.0096 | 0.006 | 0.607 | 84.96 |  | 0 | 0 | 0
Cable491 | Bus887 | Bus888 | Cable | 0 A | 0.0092 | 0.0057 | 0.582 | 84.93 |  | 0 | 0 | 0
Cable492 | Bus888 | Bus889 | Cable | 0 A | 0.0188 | 0.0117 | 1.188 | 84.95 |  | 0 | 0 | 0
Cable493 | Bus892 | Bus889 | Cable | 0 A | 0.503 | 0.315 | 31.79 | 84.76 |  | 0 | 0.0005 | 0.0494
Cable494 | Bus892 | Bus891 | Cable | 0 A | 0.0841 | 0.0535 | 5.34 | 84.39 |  | 0 | 0 | 0.0003
Cable495 | Bus893 | Bus892 | Cable | 0 A | 0.587 | 0.368 | 37.13 | 84.71 |  | 0 | 0.0001 | 0.009
Cable496 | Bus896 | Bus893 | Cable | 0 A | 0.596 | 0.374 | 37.72 | 84.71 |  | 0 | 0.0003 | 0.0317
Cable497 | Bus896 | Bus895 | Cable | 0 A | 0.0611 | 0.038 | 3.854 | 84.93 |  | 0 | 0 | 0.0001
Cable498 | Bus899 | Bus896 | Cable | 0 A | 0.658 | 0.412 | 41.57 | 84.73 |  | 0.01 | 0.0008 | 0.0809
Cable499 | Bus898 | Bus899 | Cable | 0 A | 0.0611 | 0.038 | 3.854 | 84.93 |  | 0 | 0 | 0
Cable500 | Bus900 | Bus899 | Cable | 0 A | 0.719 | 0.45 | 45.42 | 84.73 |  | 0.01 | 0.002 | 0.203
Cable501 | Bus905 | Bus900 | Cable | 0 A | 0.841 | 0.526 | 53.13 | 84.76 |  | 0 | 0.0006 | 0.0642
Cable502 | Bus904 | Bus903 | Cable | 0 A | 0.192 | 0.12 | 12.13 | 84.93 |  | 0 | 0 | 0.0029
Cable503 | Bus905 | Bus904 | Cable | 0 A | 0.385 | 0.239 | 24.26 | 84.93 |  | 0 | 0.0001 | 0.005
Cable504 | Bus906 | Bus905 | Cable | 0 A | 1.226 | 0.766 | 77.39 | 84.81 |  | 0.01 | 0.0016 | 0.164
Cable505 | Bus907 | Bus906 | Cable | 0 A | 2.764 | 1.86 | 178.4 | 82.96 |  | 0.01 | 0.0051 | 0.51
Cable506 | Bus909 | Bus907 | Cable | 0 A | 4.298 | 2.818 | 275.1 | 83.63 |  | 0 | 0.0044 | 0.436
Cable507 | Bus909 | Bus912 | Cable | 0 A | 4.301 | 2.82 | 275.3 | 83.62 |  | 0.01 | 0.0047 | 0.473
Cable508 | Bus912 | Bus911 | Cable | 0 A | 0.0842 | 0.0528 | 5.324 | 84.71 |  | 0 | 0 | 0.0003
Cable509 | Bus912 | Bus913 | Cable | 0 A | 4.385 | 2.874 | 280.7 | 83.63 |  | 0.01 | 0.0129 | 1.29
Cable510 | Bus914 | Bus913 | Cable | 0 A | 4.945 | 3.224 | 315.9 | 83.77 |  | 0.02 | 0.0196 | 1.96
Cable511 | Bus915 | Bus914 | Cable | 0 A | 5.137 | 3.348 | 328.1 | 83.78 |  | 0.03 | 0.0384 | 3.84
Cable512 | Bus915 | Bus917 | Cable | 0 A | 5.584 | 3.625 | 356.2 | 83.87 |  | 0 | 0.001 | 0.099
Cable513 | Bus917 | Bus920 | Cable | 0 A | 5.668 | 3.686 | 361.5 | 83.84 |  | 0.06 | 0.0765 | 7.65
Cable514 | Bus919 | Bus920 | Cable | 0 A | 0.0608 | 0.0384 | 3.842 | 84.57 |  | 0 | 0 | 0.0002
Cable515 | Bus920 | Bus921 | Cable | 0 A | 5.729 | 3.726 | 365.4 | 83.83 |  | 0.01 | 0.0166 | 1.66
Cable516 | Bus921 | Bus922 | Cable | 0 A | 5.977 | 3.896 | 381.4 | 83.77 |  | 0.02 | 0.0204 | 2.04
Cable517 | Bus922 | Bus923 | Cable | 0 A | 6.068 | 3.959 | 387.1 | 83.75 |  | 0.03 | 0.0465 | 4.65
Cable518 | Bus923 | Bus925 | Cable | 0 A | 6.068 | 3.959 | 387.1 | 83.75 |  | 0 | 0.0017 | 0.171
Cable520 | Bus932 | Bus829 | Cable | 0 A | 1.279 | 0.799 | 80.77 | 84.82 |  | 0 | 0.0006 | 0.0603
Cable521 | Bus935 | Bus932 | Cable | 0 A | 1.249 | 0.78 | 78.84 | 84.82 |  | 0 | 0.0013 | 0.132
Cable522 | Bus937 | Bus935 | Cable | 0 A | 1.203 | 0.751 | 75.94 | 84.82 |  | 0 | 0.0012 | 0.118
Cable523 | Bus941 | Bus937 | Cable | 0 A | 1.142 | 0.713 | 72.11 | 84.84 |  | 0.01 | 0.0021 | 0.215
Cable524 | Bus946 | Bus941 | Cable | 0 A | 0.0304 | 0.019 | 1.923 | 84.77 |  | 0 | 0 | 0.0001
Cable525 | Bus949 | Bus941 | Cable | 0 A | 1.081 | 0.675 | 68.26 | 84.85 |  | 0 | 0.0007 | 0.0732
Cable526 | Bus951 | Bus949 | Cable | 0 A | 1.072 | 0.669 | 67.68 | 84.85 |  | 0.02 | 0.0039 | 0.391
Cable527 | Bus953 | Bus951 | Cable | 0 A | 0.992 | 0.617 | 62.57 | 84.9 |  | 0.01 | 0.003 | 0.302
Cable528 | Bus953 | Bus979 | Cable | 0 A | 0.0092 | 0.0057 | 0.581 | 84.93 |  | 0 | 0 | 0
Cable529 | Bus958 | Bus953 | Cable | 0 A | 0.86 | 0.535 | 54.29 | 84.91 |  | 0.01 | 0.0016 | 0.16
Cable530 | Bus958 | Bus959 | Cable | 0 A | 0.154 | 0.0962 | 9.746 | 84.86 |  | 0 | 0 | 0.0028
Cable532 | Bus961 | Bus959 | Cable | 0 A | 0.145 | 0.0905 | 9.165 | 84.85 |  | 0 | 0 | 0.0022
Cable533 | Bus961 | Bus964 | Cable | 0 A | 0.136 | 0.0845 | 8.559 | 84.85 |  | 0 | 0.0001 | 0.0064
Cable534 | Bus964 | Bus966 | Cable | 0 A | 0.0398 | 0.0247 | 2.508 | 84.98 |  | 0 | 0 | 0.0002
Cable535 | Bus966 | Bus977 | Cable | 0 A | 0.0306 | 0.019 | 1.928 | 84.99 |  | 0 | 0 | 0.0002
Cable537 | Bus974 | Bus966 | Cable | 0 A | 0.0092 | 0.0057 | 0.58 | 84.93 |  | 0 | 0 | 0
Cable538 | Bus980 | Bus958 | Cable | 0 A | 0.706 | 0.439 | 44.54 | 84.93 |  | 0.01 | 0.0016 | 0.158
Cable539 | Bus982 | Bus980 | Cable | 0 A | 0.649 | 0.403 | 40.93 | 84.94 |  | 0 | 0 | 0.0024
Cable540 | Bus983 | Bus982 | Cable | 0 A | 0.0857 | 0.0532 | 5.405 | 84.95 |  | 0 | 0 | 0.001
Cable541 | Bus987 | Bus983 | Cable | 0 A | 0.0704 | 0.0437 | 4.439 | 84.95 |  | 0 | 0 | 0.0007
Cable542 | Bus983 | Bus985 | Cable | 0 A | 0.0153 | 0.0095 | 0.966 | 84.93 |  | 0 | 0 | 0.0001
Cable543 | Bus987 | Bus991 | Cable | 0 A | 0.0153 | 0.0095 | 0.966 | 84.93 |  | 0 | 0 | 0
Cable544 | Bus993 | Bus987 | Cable | 0 A | 0.0551 | 0.0342 | 3.474 | 84.95 |  | 0 | 0 | 0.0007
Cable545 | Bus993 | Bus994 | Cable | 0 A | 0.0398 | 0.0247 | 2.507 | 84.96 |  | 0 | 0 | 0.0004
Cable546 | Bus996 | Bus994 | Cable | 0 A | 0.0306 | 0.019 | 1.927 | 84.97 |  | 0 | 0 | 0.0003
Cable548 | Bus1002 | Bus993 | Cable | 0 A | 0.0153 | 0.0095 | 0.966 | 84.93 |  | 0 | 0 | 0
Cable549 | Bus1004 | Bus982 | Cable | 0 A | 0.563 | 0.35 | 35.52 | 84.94 |  | 0 | 0.0003 | 0.0337
Cable550 | Bus1004 | Bus1005 | Cable | 0 A | 0.0642 | 0.0399 | 4.048 | 84.93 |  | 0 | 0 | 0.0008
Cable551 | Bus1005 | Bus1008 | Cable | 0 A | 0.0031 | 0.0019 | 0.195 | 84.93 |  | 0 | 0 | 0
Cable552 | Bus1010 | Bus1005 | Cable | 0 A | 0.0611 | 0.0379 | 3.852 | 84.93 |  | 0 | 0 | 0.0002
Cable553 | Bus1010 | Bus1011 | Cable | 0 A | 0.0305 | 0.019 | 1.926 | 84.93 |  | 0 | 0 | 0
Cable554 | Bus1010 | Bus1013 | Cable | 0 A | 0.0305 | 0.019 | 1.926 | 84.93 |  | 0 | 0 | 0.0001
Cable555 | Bus1016 | Bus1004 | Cable | 0 A | 0.499 | 0.31 | 31.47 | 84.94 |  | 0 | 0.0002 | 0.0172
Cable556 | Bus1016 | Bus1018 | Cable | 0 A | 0.0305 | 0.019 | 1.926 | 84.93 |  | 0 | 0 | 0.0002
Cable557 | Bus1020 | Bus1016 | Cable | 0 A | 0.468 | 0.291 | 29.55 | 84.94 |  | 0.01 | 0.0006 | 0.058
Cable558 | Bus1020 | Bus1022 | Cable | 0 A | 0.122 | 0.0759 | 7.704 | 84.93 |  | 0 | 0 | 0.0008
Cable559 | Bus1024 | Bus1020 | Cable | 0 A | 0.346 | 0.215 | 21.84 | 84.95 |  | 0 | 0 | 0.0029
Cable560 | Bus1031 | Bus1024 | Cable | 0 A | 0.275 | 0.171 | 17.35 | 84.95 |  | 0 | 0.0002 | 0.0163
Cable561 | Bus1024 | Bus1025 | Cable | 0 A | 0.0713 | 0.0442 | 4.497 | 84.98 |  | 0 | 0 | 0.0003
Cable562 | Bus1025 | Bus1026 | Cable | 0 A | 0.0407 | 0.0253 | 2.57 | 84.98 |  | 0 | 0 | 0.0004
Cable563 | Bus1025 | Bus1027 | Cable | 0 A | 0.0306 | 0.019 | 1.927 | 84.98 |  | 0 | 0 | 0.0001
Cable564 | Bus1035 | Bus1031 | Cable | 0 A | 0.214 | 0.133 | 13.49 | 84.94 |  | 0 | 0.0001 | 0.0057
Cable565 | Bus1041 | Bus1035 | Cable | 0 A | 0.0153 | 0.0095 | 0.966 | 84.93 |  | 0 | 0 | 0.0001
Cable566 | Bus1043 | Bus1035 | Cable | 0 A | 0.183 | 0.114 | 11.56 | 84.94 |  | 0 | 0.0001 | 0.0059
Cable567 | Bus1043 | Bus1045 | Cable | 0 A | 0.0305 | 0.019 | 1.926 | 84.93 |  | 0 | 0 | 0.0001
Cable568 | Bus1047 | Bus1043 | Cable | 0 A | 0.153 | 0.0949 | 9.636 | 84.94 |  | 0 | 0.0001 | 0.0056
Cable569 | Bus1047 | Bus1049 | Cable | 0 A | 0.0305 | 0.019 | 1.926 | 84.93 |  | 0 | 0 | 0
Cable570 | Bus1051 | Bus1047 | Cable | 0 A | 0.122 | 0.0759 | 7.71 | 84.95 |  | 0 | 0 | 0.0039
Cable571 | Bus1051 | Bus1052 | Cable | 0 A | 0.0305 | 0.019 | 1.926 | 84.93 |  | 0 | 0 | 0.0002
Cable572 | Bus1054 | Bus1051 | Cable | 0 A | 0.0917 | 0.0569 | 5.784 | 84.95 |  | 0 | 0 | 0.0001
Cable573 | Bus1055 | Bus1054 | Cable | 0 A | 0.0305 | 0.019 | 1.926 | 84.93 |  | 0 | 0 | 0
Cable574 | Bus1057 | Bus1054 | Cable | 0 A | 0.0612 | 0.038 | 3.858 | 84.96 |  | 0 | 0 | 0.0014
Cable575 | Bus1058 | Bus1057 | Cable | 0 A | 0.0153 | 0.0095 | 0.966 | 84.93 |  | 0 | 0 | 0
Cable576 | Bus1061 | Bus1057 | Cable | 0 A | 0.0459 | 0.0285 | 2.893 | 84.97 |  | 0 | 0 | 0.0006
Cable577 | Bus1064 | Bus1061 | Cable | 0 A | 0.0153 | 0.0095 | 0.966 | 84.97 |  | 0 | 0 | 0.0001
T327 | Bus789 | Bus788 | Transf. 2W | 0.005 MVA | 0.0291 | 0.0185 | 1.879 | 84.35 | 683.3 | 0.82 | 0.0256 | 0.512
T328 | Bus791 | Bus790 | Transf. 2W | 0.025 MVA | 0.003 | 0.0019 | 0.192 | 84.99 | 14.1 | 0.02 | 0.0001 | 0.0011
T329 | Bus793 | Bus792 | Transf. 2W | 0.025 MVA | 0.182 | 0.117 | 11.8 | 84.18 | 856.2 | 1.03 | 0.202 | 4.04
T330 | Bus795 | Bus794 | Transf. 2W | 0.025 MVA | 0.0093 | 0.0058 | 0.596 | 84.96 | 43.7 | 0.05 | 0.0005 | 0.0103
T331 | Bus797 | Bus796 | Transf. 2W | 0.025 MVA | 0.0089 | 0.0055 | 0.571 | 84.96 | 41.8 | 0.05 | 0.0005 | 0.0094
T332 | Bus800 | Bus799 | Transf. 2W | 0.025 MVA | 0.0093 | 0.0058 | 0.596 | 84.96 | 43.7 | 0.05 | 0.0005 | 0.0103
T333 | Bus803 | Bus802 | Transf. 2W | 0.005 MVA | 0.003 | 0.0019 | 0.192 | 84.93 | 70.3 | 0.08 | 0.0003 | 0.0053
T334 | Bus806 | Bus805 | Transf. 2W | 0.005 MVA | 0.003 | 0.0019 | 0.192 | 84.93 | 70.3 | 0.08 | 0.0003 | 0.0053
T335 | Bus809 | Bus808 | Transf. 2W | 0.315 MVA | 0.193 | 0.12 | 12.14 | 84.94 | 72 | 0.08 | 0.017 | 0.339
T336 | Bus811 | Bus810 | Transf. 2W | 0.315 MVA | 0.193 | 0.12 | 12.14 | 84.94 | 72 | 0.08 | 0.017 | 0.339
T337 | Bus814 | Bus813 | Transf. 2W | 0.1 MVA | 0.0613 | 0.0381 | 3.858 | 84.93 | 72.1 | 0.08 | 0.0054 | 0.108
T338 | Bus816 | Bus815 | Transf. 2W | 0.315 MVA | 0.193 | 0.12 | 12.14 | 84.94 | 71.9 | 0.08 | 0.017 | 0.339
T339 | Bus823 | Bus817 | Transf. 2W | 0.2 MVA | 0.122 | 0.076 | 7.713 | 84.93 | 72 | 0.08 | 0.0108 | 0.216
T340 | Bus819 | Bus818 | Transf. 2W | 0.2 MVA | 0.122 | 0.076 | 7.713 | 84.93 | 72 | 0.08 | 0.0108 | 0.216
T341 | Bus821 | Bus820 | Transf. 2W | 0.2 MVA | 0.122 | 0.076 | 7.713 | 84.93 | 72 | 0.08 | 0.0108 | 0.216
T342 | Bus825 | Bus824 | Transf. 2W | 0.315 MVA | 0.193 | 0.12 | 12.13 | 84.94 | 71.9 | 0.08 | 0.0169 | 0.339
T343 | Bus830 | Bus826 | Transf. 2W | 0.1 MVA | 0.0612 | 0.038 | 3.855 | 84.93 | 71.9 | 0.08 | 0.0054 | 0.108
T344 | Bus828 | Bus827 | Transf. 2W | 0.315 MVA | 0.193 | 0.12 | 12.18 | 84.93 | 72.2 | 0.08 | 0.0171 | 0.342
T345 | Bus906 | Bus831 | Transf. 2W | 0.315 MVA | 0.193 | 0.12 | 12.18 | 84.93 | 72.2 | 0.08 | 0.0171 | 0.342
T346 | Bus833 | Bus832 | Transf. 2W | 0.315 MVA | 0.177 | 0.11 | 11.66 | 84.93 | 66.1 | 0.08 | 0.0156 | 0.313
T347 | Bus840 | Bus834 | Transf. 2W | 0.315 MVA | 0.177 | 0.11 | 11.66 | 84.93 | 66.1 | 0.08 | 0.0156 | 0.313
T348 | Bus836 | Bus835 | Transf. 2W | 0.315 MVA | 0.195 | 0.121 | 13.17 | 84.92 | 72.7 | 0.09 | 0.02 | 0.399
T349 | Bus838 | Bus837 | Transf. 2W | 0.315 MVA | 0.177 | 0.11 | 11.66 | 84.93 | 66.1 | 0.08 | 0.0156 | 0.313
T350 | Bus842 | Bus841 | Transf. 2W | 0.05 MVA | 0.202 | 0.127 | 13.37 | 84.58 | 475 | 6.33 | 0.114 | 2.28
T351 | Bus845 | Bus844 | Transf. 2W | 0.1 MVA | 0.0622 | 0.0387 | 4.099 | 84.93 | 73.2 | 0.09 | 0.0061 | 0.122
T352 | Bus849 | Bus846 | Transf. 2W | 0.315 MVA | 0.177 | 0.11 | 11.66 | 84.93 | 66.1 | 0.08 | 0.0156 | 0.313
T353 | Bus848 | Bus847 | Transf. 2W | 0.315 MVA | 0.177 | 0.11 | 11.66 | 84.93 | 66.1 | 0.08 | 0.0156 | 0.313
T354 | Bus900 | Bus851 | Transf. 2W | 0.2 MVA | 0.122 | 0.076 | 7.71 | 84.93 | 71.9 | 0.08 | 0.0108 | 0.215
T355 | Bus893 | Bus852 | Transf. 2W | 0.015 MVA | 0.0092 | 0.0057 | 0.581 | 84.93 | 72.2 | 0.08 | 0.0008 | 0.0163
T356 | Bus889 | Bus853 | Transf. 2W | 0.1 MVA | 0.0611 | 0.038 | 3.854 | 84.93 | 71.9 | 0.08 | 0.0054 | 0.108
T357 | Bus866 | Bus854 | Transf. 2W | 0.025 MVA | 0.0096 | 0.006 | 0.607 | 84.96 | 45.3 | 0.05 | 0.0005 | 0.0107
T358 | Bus865 | Bus855 | Transf. 2W | 0.015 MVA | 0.0804 | 0.0511 | 5.103 | 84.42 | 630.3 | 0.74 | 0.0629 | 1.26
T359 | Bus857 | Bus856 | Transf. 2W | 0.015 MVA | 0.0081 | 0.0051 | 0.514 | 84.94 | 63.9 | 0.07 | 0.0006 | 0.0128
T360 | Bus859 | Bus858 | Transf. 2W | 0.05 MVA | 0.0305 | 0.019 | 1.927 | 84.93 | 71.9 | 0.08 | 0.0027 | 0.0538
T361 | Bus861 | Bus860 | Transf. 2W | 0.015 MVA | 0.0092 | 0.0057 | 0.581 | 84.93 | 72.2 | 0.08 | 0.0008 | 0.0163
T362 | Bus863 | Bus862 | Transf. 2W | 0.15 MVA | 0.0815 | 0.0506 | 5.138 | 84.94 | 63.9 | 0.07 | 0.0064 | 0.128
T363 | Bus876 | Bus867 | Transf. 2W | 0.05 MVA | 0.0306 | 0.019 | 1.928 | 84.93 | 71.9 | 0.08 | 0.0027 | 0.0539
T364 | Bus869 | Bus868 | Transf. 2W | 0.05 MVA | 0.0316 | 0.0196 | 1.994 | 84.93 | 74.4 | 0.09 | 0.0029 | 0.0577
T365 | Bus871 | Bus870 | Transf. 2W | 0.015 MVA | 0.0804 | 0.0511 | 5.103 | 84.42 | 630.2 | 0.74 | 0.0629 | 1.26
T366 | Bus873 | Bus872 | Transf. 2W | 0.05 MVA | 0.0305 | 0.019 | 1.927 | 84.93 | 71.9 | 0.08 | 0.0027 | 0.0538
T367 | Bus878 | Bus877 | Transf. 2W | 0.025 MVA | 0.0153 | 0.0095 | 0.966 | 84.93 | 72.1 | 0.08 | 0.0014 | 0.0271
T368 | Bus881 | Bus880 | Transf. 2W | 0.025 MVA | 0.0153 | 0.0095 | 0.966 | 84.93 | 72.1 | 0.08 | 0.0014 | 0.0271
T369 | Bus885 | Bus884 | Transf. 2W | 0.025 MVA | 0.0096 | 0.006 | 0.607 | 84.96 | 45.3 | 0.05 | 0.0005 | 0.0107
T370 | Bus887 | Bus886 | Transf. 2W | 0.015 MVA | 0.0092 | 0.0057 | 0.582 | 84.93 | 72.3 | 0.08 | 0.0008 | 0.0164
T371 | Bus891 | Bus890 | Transf. 2W | 0.015 MVA | 0.0841 | 0.0535 | 5.34 | 84.39 | 659.3 | 0.78 | 0.0689 | 1.38
T372 | Bus895 | Bus894 | Transf. 2W | 0.1 MVA | 0.0611 | 0.038 | 3.854 | 84.93 | 71.9 | 0.08 | 0.0054 | 0.108
T373 | Bus898 | Bus897 | Transf. 2W | 0.1 MVA | 0.0611 | 0.038 | 3.854 | 84.93 | 71.9 | 0.08 | 0.0054 | 0.108
T374 | Bus904 | Bus901 | Transf. 2W | 0.315 MVA | 0.192 | 0.12 | 12.13 | 84.94 | 71.8 | 0.08 | 0.0169 | 0.339
T375 | Bus903 | Bus902 | Transf. 2W | 0.315 MVA | 0.192 | 0.12 | 12.13 | 84.94 | 71.8 | 0.08 | 0.0169 | 0.339
T376 | Bus908 | Bus909 | Transf. 2W | 0.005 MVA | 0.0031 | 0.0019 | 0.195 | 84.93 | 72.9 | 0.08 | 0.0003 | 0.0055
T377 | Bus911 | Bus910 | Transf. 2W | 0.315 MVA | 0.0842 | 0.0528 | 5.324 | 84.71 | 31.5 | 0.37 | 0.0326 | 0.653
T378 | Bus917 | Bus916 | Transf. 2W | 0.05 MVA | 0.0843 | 0.0526 | 5.318 | 84.82 | 198.3 | 0.23 | 0.0205 | 0.41
T379 | Bus919 | Bus918 | Transf. 2W | 0.015 MVA | 0.0608 | 0.0384 | 3.842 | 84.57 | 476.3 | 0.56 | 0.0357 | 0.714
T381 | Bus925 | Bus924 | Transf. 2W | 0.015 MVA | 0.0306 | 0.0191 | 1.928 | 84.78 | 239.9 | 0.28 | 0.009 | 0.18
T382 | Bus926 | Bus925 | Transf. 2W | 0.5 MVA | 6.11 | 4.198 | 129.7 | 82.42 | 1456.3 | 1.77 | 10.98 | 219.5
T384 | Bus922 | Bus931 | Transf. 2W | 0.015 MVA | 0.0911 | 0.058 | 5.774 | 84.35 | 714 | 0.84 | 0.0806 | 1.61
T386 | Bus932 | Bus934 | Transf. 2W | 0.05 MVA | 0.0306 | 0.019 | 1.928 | 84.93 | 71.9 | 0.08 | 0.0027 | 0.0539
T388 | Bus935 | Bus936 | Transf. 2W | 0.075 MVA | 0.0459 | 0.0285 | 2.894 | 84.93 | 72 | 0.08 | 0.004 | 0.081
T389 | Bus937 | Bus940 | Transf. 2W | 0.0141 MVA | 0.0605 | 0.0383 | 3.835 | 84.54 | 504.8 | 0.59 | 0.0378 | 0.756
T391 | Bus946 | Bus947 | Transf. 2W | 0.0141 MVA | 0.0304 | 0.019 | 1.923 | 84.77 | 253.9 | 0.3 | 0.0095 | 0.19
T392 | Bus941 | Bus948 | Transf. 2W | 0.05 MVA | 0.0306 | 0.019 | 1.927 | 84.93 | 71.9 | 0.08 | 0.0027 | 0.0539
T393 | Bus949 | Bus950 | Transf. 2W | 0.015 MVA | 0.0092 | 0.0057 | 0.581 | 84.93 | 72.2 | 0.08 | 0.0008 | 0.0163
T394 | Bus951 | Bus952 | Transf. 2W | 0.015 MVA | 0.0804 | 0.0511 | 5.104 | 84.42 | 630.4 | 0.74 | 0.063 | 1.26
T395 | Bus979 | Bus955 | Transf. 2W | 0.015 MVA | 0.0092 | 0.0057 | 0.581 | 84.93 | 72.2 | 0.08 | 0.0008 | 0.0163
T397 | Bus953 | Bus957 | Transf. 2W | 0.2 MVA | 0.122 | 0.0759 | 7.707 | 84.93 | 71.9 | 0.08 | 0.0108 | 0.215
T398 | Bus959 | Bus960 | Transf. 2W | 0.015 MVA | 0.0092 | 0.0057 | 0.581 | 84.93 | 72.2 | 0.08 | 0.0008 | 0.0163
T399 | Bus961 | Bus962 | Transf. 2W | 0.05 MVA | 0.0096 | 0.006 | 0.607 | 84.98 | 22.6 | 0.03 | 0.0003 | 0.0053
T400 | Bus964 | Bus965 | Transf. 2W | 0.05 MVA | 0.0958 | 0.0599 | 6.051 | 84.8 | 225.2 | 0.26 | 0.0265 | 0.531
T402 | Bus974 | Bus976 | Transf. 2W | 0.015 MVA | 0.0092 | 0.0057 | 0.58 | 84.93 | 72.2 | 0.08 | 0.0008 | 0.0163
T403 | Bus977 | Bus978 | Transf. 2W | 0.3 MVA | 0.0306 | 0.019 | 1.928 | 84.99 | 12 | 0.01 | 0.0004 | 0.009
T404 | Bus980 | Bus981 | Transf. 2W | 0.05 MVA | 0.0572 | 0.0357 | 3.614 | 84.88 | 134.7 | 0.16 | 0.0095 | 0.189
T405 | Bus985 | Bus986 | Transf. 2W | 0.025 MVA | 0.0153 | 0.0095 | 0.966 | 84.93 | 72 | 0.08 | 0.0014 | 0.027
T406 | Bus991 | Bus992 | Transf. 2W | 0.025 MVA | 0.0153 | 0.0095 | 0.966 | 84.93 | 72 | 0.08 | 0.0014 | 0.027
T407 | Bus996 | Bus1000 | Transf. 2W | 0.1 MVA | 0.0306 | 0.019 | 1.927 | 84.97 | 35.9 | 0.04 | 0.0013 | 0.0269
T408 | Bus994 | Bus999 | Transf. 2W | 0.015 MVA | 0.0092 | 0.0057 | 0.58 | 84.93 | 72.2 | 0.08 | 0.0008 | 0.0163
T409 | Bus1002 | Bus1003 | Transf. 2W | 0.025 MVA | 0.0153 | 0.0095 | 0.966 | 84.93 | 72.1 | 0.08 | 0.0014 | 0.0271
T410 | Bus1008 | Bus1009 | Transf. 2W | 0.005 MVA | 0.0031 | 0.0019 | 0.195 | 84.93 | 72.8 | 0.08 | 0.0003 | 0.0055
T411 | Bus1011 | Bus1012 | Transf. 2W | 0.05 MVA | 0.0305 | 0.019 | 1.926 | 84.93 | 71.8 | 0.08 | 0.0027 | 0.0538
T412 | Bus1013 | Bus1015 | Transf. 2W | 0.05 MVA | 0.0305 | 0.019 | 1.926 | 84.93 | 71.8 | 0.08 | 0.0027 | 0.0538
T413 | Bus1018 | Bus1019 | Transf. 2W | 0.05 MVA | 0.0305 | 0.019 | 1.926 | 84.93 | 71.8 | 0.08 | 0.0027 | 0.0538
T414 | Bus1022 | Bus1023 | Transf. 2W | 0.2 MVA | 0.122 | 0.0759 | 7.704 | 84.93 | 71.8 | 0.08 | 0.0108 | 0.215
T415 | Bus1026 | Bus1028 | Transf. 2W | 0.2 MVA | 0.0407 | 0.0253 | 2.57 | 84.98 | 24 | 0.03 | 0.0012 | 0.0239
T416 | Bus1027 | Bus1030 | Transf. 2W | 0.15 MVA | 0.0306 | 0.019 | 1.927 | 84.98 | 24 | 0.03 | 0.0009 | 0.018
T417 | Bus1031 | Bus1034 | Transf. 2W | 0.5 MVA | 0.0611 | 0.0379 | 3.855 | 84.99 | 14.4 | 0.02 | 0.0011 | 0.0215
T418 | Bus1035 | Bus1036 | Transf. 2W | 0.025 MVA | 0.0153 | 0.0095 | 0.966 | 84.93 | 72 | 0.08 | 0.0014 | 0.027
T420 | Bus1041 | Bus1042 | Transf. 2W | 0.025 MVA | 0.0153 | 0.0095 | 0.966 | 84.93 | 72 | 0.08 | 0.0014 | 0.027
T421 | Bus1045 | Bus1046 | Transf. 2W | 0.05 MVA | 0.0305 | 0.019 | 1.926 | 84.93 | 71.8 | 0.08 | 0.0027 | 0.0538
T422 | Bus1049 | Bus1050 | Transf. 2W | 0.05 MVA | 0.0305 | 0.019 | 1.926 | 84.93 | 71.8 | 0.08 | 0.0027 | 0.0538
T423 | Bus1052 | Bus1053 | Transf. 2W | 0.05 MVA | 0.0305 | 0.019 | 1.926 | 84.93 | 71.8 | 0.08 | 0.0027 | 0.0538
T424 | Bus1055 | Bus1056 | Transf. 2W | 0.05 MVA | 0.0305 | 0.019 | 1.926 | 84.93 | 71.8 | 0.08 | 0.0027 | 0.0538
T425 | Bus1058 | Bus1060 | Transf. 2W | 0.025 MVA | 0.0153 | 0.0095 | 0.966 | 84.93 | 72 | 0.08 | 0.0014 | 0.027
T427 | Bus1061 | Bus1063 | Transf. 2W | 0.1 MVA | 0.0305 | 0.019 | 1.927 | 84.97 | 35.9 | 0.04 | 0.0013 | 0.0269
T428 | Bus1064 | Bus1065 | Transf. 2W | 0.05 MVA | 0.0153 | 0.0095 | 0.966 | 84.97 | 36 | 0.04 | 0.0007 | 0.0135

## Load
ID | Terminal Bus | Type | Rating/Limit | Rated kV | kW | kvar | Amp | % PF | % Loading | Vterminal
Lump274 | Bus788 | Lumped | 37.5 kVA | 0.415 | 29.04 | 18 | 49.8 | 85 | 95.5 | 95.45
Lump275 | Bus790 | Lumped | 3.8 kVA | 0.415 | 2.99 | 1.85 | 5.089 | 85 | 96.3 | 96.25
Lump276 | Bus792 | Lumped | 236 kVA | 0.415 | 181.9 | 112.8 | 312.7 | 85 | 95.2 | 95.23
Lump277 | Bus794 | Lumped | 11.8 kVA | 0.415 | 9.29 | 5.75 | 15.8 | 85 | 96.2 | 96.22
Lump278 | Bus796 | Lumped | 11.3 kVA | 0.415 | 8.89 | 5.51 | 15.13 | 85 | 96.2 | 96.22
Lump279 | Bus799 | Lumped | 11.8 kVA | 0.415 | 9.29 | 5.76 | 15.8 | 85 | 96.2 | 96.22
Lump280 | Bus802 | Lumped | 3.8 kVA | 0.415 | 2.99 | 1.85 | 5.085 | 85 | 96.2 | 96.19
Lump281 | Bus805 | Lumped | 3.8 kVA | 0.415 | 2.99 | 1.85 | 5.085 | 85 | 96.2 | 96.19
Lump282 | Bus808 | Lumped | 236 kVA | 0.415 | 192.7 | 119.4 | 321.8 | 85 | 98 | 98.01
Lump283 | Bus810 | Lumped | 236 kVA | 0.415 | 192.7 | 119.4 | 321.8 | 85 | 98 | 98.02
Lump284 | Bus813 | Lumped | 75 kVA | 0.415 | 61.25 | 37.96 | 102.3 | 85 | 98 | 98.02
Lump285 | Bus815 | Lumped | 236 kVA | 0.415 | 192.6 | 119.4 | 321.7 | 85 | 98 | 97.98
Lump286 | Bus817 | Lumped | 150 kVA | 0.415 | 122.4 | 75.83 | 204.4 | 85 | 98 | 97.97
Lump287 | Bus818 | Lumped | 150 kVA | 0.415 | 122.4 | 75.83 | 204.4 | 85 | 98 | 97.96
Lump288 | Bus820 | Lumped | 150 kVA | 0.415 | 122.4 | 75.83 | 204.4 | 85 | 98 | 97.96
Lump289 | Bus824 | Lumped | 236 kVA | 0.415 | 192.5 | 119.3 | 321.6 | 85 | 98 | 97.97
Lump290 | Bus826 | Lumped | 75 kVA | 0.415 | 61.15 | 37.9 | 102.2 | 85 | 97.9 | 97.94
Lump291 | Bus827 | Lumped | 237 kVA | 0.415 | 193.2 | 119.8 | 322.9 | 85 | 97.9 | 97.94
Lump292 | Bus831 | Lumped | 237 kVA | 0.415 | 193.2 | 119.7 | 322.9 | 85 | 97.9 | 97.93
Lump293 | Bus832 | Lumped | 237 kVA | 0.415 | 176.9 | 109.6 | 309 | 85 | 93.7 | 93.7
Lump294 | Bus834 | Lumped | 237 kVA | 0.415 | 176.9 | 109.6 | 308.9 | 85 | 93.7 | 93.7
Lump295 | Bus835 | Lumped | 237 kVA | 0.415 | 194.7 | 120.7 | 349.1 | 85 | 105.9 | 91.29
Lump296 | Bus837 | Lumped | 237 kVA | 0.415 | 176.9 | 109.6 | 308.9 | 85 | 93.7 | 93.7
Lump297 | Bus841 | Lumped | 237 kVA | 0.415 | 201.9 | 125.1 | 330.1 | 85 | 100.1 | 100.11
Lump298 | Bus844 | Lumped | 75 kVA | 0.415 | 62.19 | 38.54 | 108.6 | 85 | 104.1 | 93.7
Lump299 | Bus846 | Lumped | 237 kVA | 0.415 | 176.9 | 109.6 | 309 | 85 | 93.7 | 93.7
Lump300 | Bus847 | Lumped | 237 kVA | 0.415 | 176.9 | 109.6 | 309 | 85 | 93.7 | 93.7
Lump301 | Bus851 | Lumped | 150 kVA | 0.415 | 122.3 | 75.77 | 204.4 | 85 | 97.9 | 97.93
Lump302 | Bus852 | Lumped | 11.3 kVA | 0.415 | 9.21 | 5.71 | 15.39 | 85 | 97.9 | 97.9
Lump303 | Bus853 | Lumped | 75 kVA | 0.415 | 61.1 | 37.87 | 102.1 | 85 | 97.9 | 97.9
Lump304 | Bus854 | Lumped | 11.8 kVA | 0.415 | 9.62 | 5.96 | 16.08 | 85 | 97.9 | 97.93
Lump305 | Bus855 | Lumped | 100 kVA | 0.415 | 80.36 | 49.8 | 135.3 | 85 | 97.2 | 97.23
Lump306 | Bus856 | Lumped | 10 kVA | 0.415 | 8.15 | 5.05 | 13.62 | 85 | 97.9 | 97.89
Lump307 | Bus858 | Lumped | 37.5 kVA | 0.415 | 30.54 | 18.93 | 51.07 | 85 | 97.9 | 97.89
Lump308 | Bus860 | Lumped | 11.3 kVA | 0.415 | 9.2 | 5.7 | 15.39 | 85 | 97.9 | 97.89
Lump309 | Bus862 | Lumped | 100 kVA | 0.415 | 81.47 | 50.49 | 136.2 | 85 | 97.9 | 97.9
Lump310 | Bus867 | Lumped | 37.5 kVA | 0.415 | 30.56 | 18.94 | 51.09 | 85 | 97.9 | 97.89
Lump311 | Bus868 | Lumped | 37.5 kVA | 0.415 | 31.61 | 19.59 | 52.85 | 85 | 101.3 | 97.89
Lump312 | Bus870 | Lumped | 100 kVA | 0.415 | 80.36 | 49.8 | 135.3 | 85 | 97.2 | 97.23
Lump313 | Bus872 | Lumped | 37.5 kVA | 0.415 | 30.55 | 18.93 | 51.07 | 85 | 97.9 | 97.89
Lump314 | Bus877 | Lumped | 18.8 kVA | 0.415 | 15.31 | 9.49 | 25.6 | 85 | 97.9 | 97.9
Lump315 | Bus880 | Lumped | 18.8 kVA | 0.415 | 15.31 | 9.49 | 25.6 | 85 | 97.9 | 97.9
Lump316 | Bus884 | Lumped | 11.8 kVA | 0.415 | 9.62 | 5.96 | 16.08 | 85 | 97.9 | 97.93
Lump317 | Bus886 | Lumped | 11.3 kVA | 0.415 | 9.22 | 5.72 | 15.42 | 85 | 98.1 | 97.9
Lump318 | Bus890 | Lumped | 100 kVA | 0.415 | 84.06 | 52.1 | 141.5 | 85 | 101.7 | 97.21
Lump319 | Bus894 | Lumped | 75 kVA | 0.415 | 61.11 | 37.87 | 102.2 | 85 | 97.9 | 97.91
Lump320 | Bus897 | Lumped | 75 kVA | 0.415 | 61.12 | 37.88 | 102.2 | 85 | 97.9 | 97.91
Lump321 | Bus901 | Lumped | 236 kVA | 0.415 | 192.4 | 119.2 | 321.5 | 85 | 97.9 | 97.93
Lump322 | Bus902 | Lumped | 236 kVA | 415 | 192.4 | 119.2 | 0.322 | 85 | 97.9 | 97.93
Lump323 | Bus908 | Lumped | 3.8 kVA | 0.415 | 3.1 | 1.92 | 5.178 | 85 | 97.9 | 97.95
Lump324 | Bus910 | Lumped | 100 kVA | 0.415 | 84.22 | 52.19 | 141.1 | 85 | 101.4 | 97.67
Lump325 | Bus916 | Lumped | 100 kVA | 0.415 | 84.28 | 52.23 | 140.9 | 85 | 101.3 | 97.87
Lump326 | Bus918 | Lumped | 75 kVA | 0.415 | 60.73 | 37.64 | 101.8 | 85 | 97.6 | 97.61
Lump327 | Bus924 | Lumped | 37.5 kVA | 0.415 | 30.58 | 18.95 | 51.1 | 85 | 98 | 97.95
Lump330 | Bus931 | Lumped | 113 kVA | 0.415 | 91.03 | 56.42 | 153 | 85 | 97.4 | 97.35
Lump331 | Bus934 | Lumped | 37.5 kVA | 0.415 | 30.57 | 18.95 | 51.09 | 85 | 97.9 | 97.94
Lump332 | Bus936 | Lumped | 56.3 kVA | 0.415 | 45.9 | 28.44 | 76.71 | 85 | 97.9 | 97.93
Lump333 | Bus940 | Lumped | 75 kVA | 0.415 | 60.5 | 37.5 | 101.6 | 85 | 97.4 | 97.42
Lump334 | Bus947 | Lumped | 37.5 kVA | 0.415 | 30.43 | 18.86 | 50.97 | 85 | 97.7 | 97.71
Lump335 | Bus948 | Lumped | 37.5 kVA | 0.415 | 30.56 | 18.94 | 51.08 | 85 | 97.9 | 97.92
Lump336 | Bus950 | Lumped | 11.3 kVA | 0.415 | 9.21 | 5.71 | 15.39 | 85 | 97.9 | 97.92
Lump337 | Bus952 | Lumped | 100 kVA | 0.415 | 80.37 | 49.81 | 135.3 | 85 | 97.2 | 97.24
Lump338 | Bus955 | Lumped | 11.3 kVA | 0.415 | 9.2 | 5.7 | 15.39 | 85 | 97.9 | 97.89
Lump339 | Bus957 | Lumped | 150 kVA | 0.415 | 122.2 | 75.71 | 204.3 | 85 | 97.9 | 97.89
Lump340 | Bus960 | Lumped | 11.3 kVA | 0.415 | 9.2 | 5.7 | 15.39 | 85 | 97.9 | 97.88
Lump341 | Bus962 | Lumped | 11.8 kVA | 0.415 | 9.62 | 5.96 | 16.08 | 85 | 97.9 | 97.93
Lump342 | Bus965 | Lumped | 118 kVA | 0.415 | 95.73 | 59.33 | 160.4 | 85 | 97.7 | 97.7
Lump343 | Bus976 | Lumped | 11.3 kVA | 0.415 | 9.2 | 5.7 | 15.39 | 85 | 97.9 | 97.87
Lump344 | Bus978 | Lumped | 37.5 kVA | 0.415 | 30.58 | 18.95 | 51.1 | 85 | 97.9 | 97.94
Lump345 | Bus981 | Lumped | 70.4 kVA | 0.415 | 57.23 | 35.47 | 95.78 | 85 | 97.8 | 97.79
Lump346 | Bus986 | Lumped | 18.8 kVA | 0.415 | 15.31 | 9.49 | 25.6 | 85 | 97.9 | 97.87
Lump347 | Bus992 | Lumped | 18.8 kVA | 0.415 | 15.31 | 9.49 | 25.6 | 85 | 97.9 | 97.87
Lump348 | Bus1000 | Lumped | 37.5 kVA | 0.415 | 30.55 | 18.94 | 51.08 | 85 | 97.9 | 97.91
Lump349 | Bus999 | Lumped | 11.3 kVA | 0.415 | 9.2 | 5.7 | 15.39 | 85 | 97.9 | 97.87
Lump350 | Bus1003 | Lumped | 18.8 kVA | 0.415 | 15.31 | 9.49 | 25.61 | 85 | 97.9 | 97.87
Lump351 | Bus1009 | Lumped | 3.8 kVA | 0.415 | 3.09 | 1.92 | 5.174 | 85 | 97.9 | 97.86
Lump352 | Bus1012 | Lumped | 37.5 kVA | 0.415 | 30.53 | 18.92 | 51.06 | 85 | 97.9 | 97.86
Lump353 | Bus1015 | Lumped | 37.5 kVA | 0.415 | 30.53 | 18.92 | 51.06 | 85 | 97.9 | 97.86
Lump354 | Bus1019 | Lumped | 37.5 kVA | 0.415 | 30.53 | 18.92 | 51.06 | 85 | 97.9 | 97.86
Lump355 | Bus1023 | Lumped | 150 kVA | 0.415 | 122.1 | 75.67 | 204.2 | 85 | 97.9 | 97.86
Lump356 | Bus1028 | Lumped | 50 kVA | 0.415 | 40.74 | 25.25 | 68.11 | 85 | 97.9 | 97.91
Lump357 | Bus1030 | Lumped | 37.5 kVA | 0.415 | 30.56 | 18.94 | 51.08 | 85 | 97.9 | 97.91
Lump358 | Bus1034 | Lumped | 75 kVA | 0.415 | 61.13 | 37.88 | 102.2 | 85 | 97.9 | 97.92
Lump359 | Bus1036 | Lumped | 18.8 kVA | 0.415 | 15.3 | 9.48 | 25.59 | 85 | 97.9 | 97.85
Lump360 | Bus1042 | Lumped | 18.8 kVA | 0.415 | 15.3 | 9.48 | 25.59 | 85 | 97.9 | 97.85
Lump361 | Bus1046 | Lumped | 37.5 kVA | 0.415 | 30.52 | 18.91 | 51.05 | 85 | 97.9 | 97.85
Lump362 | Bus1050 | Lumped | 37.5 kVA | 0.415 | 30.52 | 18.91 | 51.05 | 85 | 97.9 | 97.85
Lump363 | Bus1053 | Lumped | 37.5 kVA | 0.415 | 30.52 | 18.91 | 51.05 | 85 | 97.8 | 97.85
Lump364 | Bus1056 | Lumped | 37.5 kVA | 0.415 | 30.52 | 18.91 | 51.05 | 85 | 97.8 | 97.85
Lump365 | Bus1060 | Lumped | 18.8 kVA | 0.415 | 15.3 | 9.48 | 25.59 | 85 | 97.8 | 97.85
Lump366 | Bus1063 | Lumped | 37.5 kVA | 0.415 | 30.54 | 18.93 | 51.07 | 85 | 97.9 | 97.89
Lump367 | Bus1065 | Lumped | 18.8 kVA | 0.415 | 15.31 | 9.49 | 25.6 | 85 | 97.9 | 97.89

## Source
ID | Rating/Limit | Rated kV | MW | Mvar | Amp | % PF | % Generation
U7 | 12.6 MVA | 33 | 6.11 | 4.198 | 129.7 | 82.42